{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":56,"n_cols":11,"rows_kept":56,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","2MXS-H"]
[]
[]
[]
[]
["","","","","","2MXS40H3V1B2","2MXS40H3V1B","2MXS40H2V1B","2MXS50H3V1B2","2MXS50H3V1B","2MXS50H2V1B"]
["Nível de pressão sonora","Aquecimento","","Nom.","dBA","48","48","","50","50"]
["","Arrefecimento","","Nom.","dBA","47","47","","48","48"]
["Acessórios standard","Manual de instalação","","","","1","1","","1","1"]
["","Saco de parafusos","","","","1","1","","1","1"]
["","Tampão de drenagem","","","","1","1","","1","1"]
["","Redutor","","","","","","","1","1"]
["Fluido frigorigéneo","Charge","","","TCO2Eq","2.5","2.5","","3.3","3.3"]
["","GWP","","","","2,087.5","2,087.5","","2,087.5","2,087.5"]
["","Carga","","","kg","1.20","1.20","","1.60","1.60"]
["","Tipo","","","","R-410A","R-410A","","R-410A","R-410A"]
["Piping connections","Diferença de nível","IU - IU","Máx.","m","7.5","7.5","","7.5","7.5"]
["","","IU - OU","Máx.","m","15","15","","15","15"]
["","Carga de refrigerante adicional","","","kg/m","0,02 (para comprimento de tubagem superior a 20m)","0,02 (para comprimento de tubagem superior a 20m)","","0,02 (para comprimento de tubagem superior a 20m)","0,02 (para comprimento de tubagem superior a 20m)"]
["","Comprimento total da tubagem","Sistema","Real","m","30","30","","30","30"]
["Compressor","Type","","","","Compressor oscilante hermético","Compressor oscilante hermético","","Compressor oscilante hermético","Compressor oscilante hermético"]
["Dimensões","Unidade","","Largura","mm","765","765","","765","765"]
["","","","Profundidade","mm","285","285","","285","285"]
["","","","Altura","mm","550","550","","550","550"]
["Peso","Unidade","","","kg","38","38","","42","42"]
["Power supply","Phase","","","","1~","1~","","1~","1~"]
["","Frequência","","","Hz","50","50","","50","50"]
["","Tensão","","","V","220-240","220-240","","220-240","220-240"]
["Notas","","","","","(1) - Contém gases fluorados com efeito de estufa","(1) - Contém gases fluorados com efeito de estufa","","(1) - Contém gases fluorados com efeito de estufa","(1) - Contém gases fluorados com efeito de estufa"]
["Dimensões","Unidade","","Altura","mm","","","550","","","550"]
["","","","Largura","mm","","","765","","","765"]
["","","","Profundidade","mm","","","285","","","285"]
["Peso","Unidade","","","kg","","","38","","","42"]
["Compressor","Type","","","","","","Compressor oscilante hermético","","","Compressor oscilante hermético"]
["Limite de funcionamento","Arrefecimento","Ambiente","Mín.","° CBs","","","10","","","10"]
["","","","Máx.","° CBs","","","46","","","46"]
["","Aquecimento","Ambiente","Mín.","° CBh","","","-15","","","-15"]
["","","","Máx.","° CBh","","","15.5","","","15.5"]
["Nível de pressão sonora","Arrefecimento","","Nom.","dBA","","","47","","","48"]
["","Aquecimento","","Nom.","dBA","","","48","","","50"]
["Fluido frigorigéneo","Tipo","","","","","","R-410A","","","R-410A"]
["","Carga","","","kg","","","1.20","","","1.60"]
["","Carga","","","tCO2Eq","","","2.5","","","3.3"]
["","GWP","","","","","","2087.5","","","2087.5"]
["Ligações de tubagens","Comprimento da tubagem","Máx.","OU - IU","m","","","20","","","20"]
["","Carga de refrigerante adicional","","","kg/m","","","0,02 (para comprimento de tubagem superior a 20m)","","","0,02 (para comprimento de tubagem superior a 20m)"]
["","Diferença de nível","IU - OU","Máx.","m","","","15","","","15"]
["","","IU - IU","Máx.","m","","","7.5","","","7.5"]
["","Comprimento total da tubagem","Sistema","Real","m","","","30","","","30"]
["Acessórios standard","Installation manual","","","","","","1","","","1"]
["","Drain plug","","","","","","1","","","1"]
["","Screw bag","","","","","","1","","","1"]
["Alimentação elétrica","Fase","","","","","","1~","","","1~"]
["Alimentação eléctrica","Frequência","","","Hz","","","50","","","50"]
["","Tensão","","","V","","","220-240","","","220-240"]
["Acessórios standard","Reducer assembly","","","","","","","","","1"]