{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":6,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWHT-Q-XSA"]
[]
[]
[]
[]
["","","","","","EWHT100Q-XSA1"]
["Capacidade de arrefecimento","Nom.","","","kW","91.68"]
["Controlo de capacidade","Método","","","","Passo"]
["Controlo da capacidade","Capacidade mínima","","","%","50"]
["Potência nominal","Arrefecimento","","Nom.","kW","21.22"]
["EER","","","","","4.32"]
["IPLV","","","","","6.66"]
["SEER","","","","","5.98"]
["Dimensões","Unidade","","Profundidade","mm","1300"]
["","","","Altura","mm","1000"]
["","","","Largura","mm","1200"]
["Peso","Peso em funcionamento","","","kg","451"]
["","Unidade","","","kg","431"]
["Envolvente","Cor","","","","Branco marfim"]
["","Material","","","","Aço galvanizado"]
["Evaporador","Perda de carga de água","Arrefecimento","Nom.","kPa","17.7"]
["Compressor","Quantidade","","","","2"]
["","Tipo","","","","Scroll"]
["Limites de funcionamento","Lado da água","Evaporador","Mín.","° CBs","-15"]
["","","","Máx.","° CBs","30"]
["Nível de potência sonora","Arrefecimento","","Nom.","dBA","80.99"]
["Nível de pressão sonora","Arrefecimento","","Nom.","dBA","65.4"]
["Fluido frigorigéneo","Tipo","","","","R-32"]
["","GWP","","","","675"]
["","Carga","","","kg","7"]
["","Circuitos","","Quantidade","","1"]
["Ligações de tubagens","Entrada/saída da água do evaporador (DE)","","","","3\""]
["Alimentação elétrica","Fase","","","","3"]
["Alimentação eléctrica","Frequência","","","Hz","50"]
["","Tensão","","","V","400"]
["","Limite de tensão","","Mín.","%","-10"]
["","","","Máx.","%","+10"]
["Unidade","Corrente inicial","","Máx.","A","221"]
["","Corrente ativa","Arrefecimento","Nom.","A","36.9"]
["","","","Máx.","A","62"]
["","Corrente máxima da unidade para medição dos fios","","","A","68"]