{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":9,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FBA-A"]
[]
[]
[]
[]
["","","","","","FBA35A2VEB","FBA50A2VEB","FBA60A2VEB","FBA71A2VEB"]
["Nível de pressão sonora","Aquecimento","","Alto","dBA","37.0","37.0","31.0","31.0"]
["","","","Médio","dBA","34.0","34.0","28.0","28.0"]
["","","","B","dBA","29.0","29.0","25.0","25.0"]
["","Arrefecimento","","Médio","dBA","32.0","32.0","28.0","28.0"]
["","","","B","dBA","29.0","29.0","25.0","25.0"]
["","","","Alto","dBA","35.0","35.0","30.0","30.0"]
["Acessórios standard","Manual de funcionamento","","","","1","1","1","1"]
["","Manual de instalação","","","","1","1","1","1"]
["","Tubo flexível de drenagem","","","","1","1","1","1"]
["","Braçadeira de metal para tubo flexível de descarga","","","","1","1","1","1"]
["","Anilha para o suporte do gancho","","","","8","8","8","8"]
["","Parafusos","","","","40","40","40","40"]
["","Isolamento para instalação","","","","2","2","2","2"]
["","Blocos de vedação","","","","5","5","5","5"]
["","Braçadeiras","","","","4","4","4","4"]
["Control systems","Wired remote control","","","","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7","BRC1D528, BRC1E53A7, BRC1E53B7, BRC1E53C7"]
["","Infrared remote control","","","","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66"]
["Piping connections","Líquido","","DE","mm","6.35","6.35","6.35","9.52"]
["","Gás","","DE","mm","9.52","12.70","12.70","15.90"]
["","Esgoto","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["Nível de potência sonora","Arrefecimento","","","dBA","60","60","56","56"]
["Dimensões","Unidade","","Largura","mm","700","700","1,000","1,000"]
["","","","Profundidade","mm","800","800","800","800"]
["","","","Altura","mm","245","245","245","245"]
["Envolvente","Material","","","","Chapa de aço galvanizado","Chapa de aço galvanizado","Chapa de aço galvanizado","Chapa de aço galvanizado"]
["","Colour","","","","Não pintado (galvanizado)","Não pintado (galvanizado)","Não pintado (galvanizado)","Não pintado (galvanizado)"]
["Peso","Unidade","","","kg","28.0","28.0","35.0","35.0"]
["Ventilador","Pressão estática disponível","","Alto","Pa","150","150","150","150"]
["","","","Nom.","Pa","30","30","30","30"]
["","Caudal de ar","Aquecimento","Alto","m³/min","15.0","15.0","18.0","18.0"]
["","","","B","m³/min","10.5","10.5","12.5","12.5"]
["","","","Médio","m³/min","12.5","12.5","15.0","15.0"]
["","","Arrefecimento","B","m³/min","10.5","10.5","12.5","12.5"]
["","","","Médio","m³/min","12.5","12.5","15.0","15.0"]
["","","","Alto","m³/min","15.0","15.0","18.0","18.0"]
["Altura de drenagem","mm","","","","625","625","625","625"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Frequência","","","Hz","50/60","50/60","50/60","50/60"]
["","Tensão","","","V","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notas","","","","","(1) - O nível de potência sonora é um valor absoluto que indica a potência que gera um determinado som.","(1) - O nível de potência sonora é um valor absoluto que indica a potência que gera um determinado som.","(1) - O nível de potência sonora é um valor absoluto que indica a potência que gera um determinado som.","(1) - O nível de potência sonora é um valor absoluto que indica a potência que gera um determinado som."]
["","","","","","(2) - Consulte o esquema separado para conhecer os dados eléctricos","(2) - Consulte o esquema separado para conhecer os dados eléctricos","(2) - Consulte o esquema separado para conhecer os dados eléctricos","(2) - Consulte o esquema separado para conhecer os dados eléctricos"]