{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":6,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DF"]
[]
[]
[]
[]
["","","","","","FWC07DAFN5V3--"]
["Capacidade de arrefecimento (condições padrão)","Capacidade sensível 4 tubos","","B","kW","3.26"]
["","","","Alto","kW","5.58"]
["","Capacidade total 4 tubos","","B","kW","4.35"]
["","","","Alto","kW","7.15"]
["Capacidade de aquecimento (condições padrão)","Capacidade 4 tubos","","B","kW","5.34"]
["","","","Alto","kW","8.82"]
["Potência absorvida","B","","","kW","0.02"]
["","Alto","","","kW","0.069"]
["Dimensões","Unidade","","Altura","mm","287"]
["","","","Largura","mm","837"]
["","","","Profundidade","mm","921"]
["Peso","Unidade","","","kg","27"]
["Ventilador","Caudal de ar","","B","m³/h","686"]
["","","","Alto","m³/h","1,296"]
["Nível total de potência sonora","B","","","dBA","36"]
["","Alto","","","dBA","52"]
["Nível de pressão sonora","B","","","dBA","23"]
["","Alto","","","dBA","39"]
["Caudal de água","Arrefecimento","","B","l/h","776"]
["","","","Alto","l/h","1,295"]
["","Aquecimento","","B","l/h","459"]
["","","","Alto","l/h","759"]
["","Perda de pressão de água","Arrefecimento","B","kPa","13"]
["","","","Alto","kPa","25"]
["","","Aquecimento","B","kPa","13"]
["","","","Alto","kPa","24"]
["Ligações de tubagens","Água","","Entrada","","3/4\" BSP (rosca fêmea)"]
["","","","Saída","","3/4\" BSP (rosca fêmea)"]
["","Esgoto","","OD","mm","VP25 (diâmetro externo 32; diâmetro interno 25)"]
["Alimentação eléctrica","Tipo","","","","230 / 1 / 50"]
["Alimentação elétrica","Fase","","","","1~"]
["Alimentação eléctrica","Frequência","","","Hz","50"]
["","Tensão","","","V","230"]
["Notas","","","","","(1) - Arrefecimento: ar 27°CBs, 19°CBh; água de entrada 7°C; água de saída 12°C"]
["","","","","","(2) - Aquecimento: 2 tubos: ar 20°CBs, 15°CBh; água de entrada 45°C; água de saída 40°C;"]
["","","","","","(3) - Aquecimento: 4 tubos: ar 20°CBs, 15°CBh; água de entrada 65°C; água de saída 55°C;"]
["","","","","","(4) - Não permita a entrada de água com temperatura inferior a 5 °C ou superior a 90 °C, isto pode danificar a unidade"]
["","","","","","(5) - Caudal de ar: 20 °C CBs, 15 °C CBh; 230 V 50 Hz 0 Pa"]