{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":8,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXM-ATV3"]
[]
[]
[]
[]
["","","","","","FWXM10AATV3","FWXM15AATV3","FWXM20AATV3"]
["Capacidade de arrefecimento","7/12 °C","","Mín.","kW","0.75","1.15","1.32"]
["","","","Méd.","kW","1.36","2.08","2.39"]
["","","","Máx.","kW","2.12","2.81","3.30"]
["Capacidade de arrefecimento sensível","7/12 °C","","Mín.","kW","0.59","0.83","1.02"]
["","","","Méd.","kW","1.04","1.51","1.84"]
["","","","Máx.","kW","1.54","2.11","2.65"]
["Capacidade de aquecimento","45/40 °C","","Mín.","kW","0.82","1.20","1.47"]
["","","","Capacidade de aquecimento-=-45/40 °C-=-Méd.-=-kW","kW","1.53","2.16","2.59"]
["","","","Máx.","kW","2.21","3.02","3.81"]
["Potência absorvida","Mín.","","","kW","0","0.01","0.01"]
["","Méd.","","","kW","0.01","0.01","0.01"]
["","Máx.","","","kW","0.02","0.02","0.03"]
["Velocidade do ventilador","Mín.","","","rpm","680.00","680.00","680.00"]
["","Méd.","","","rpm","1100.00","1100.00","1100.00"]
["","Velocidade do ventilador-=-Máx.-=-rpm","","","rpm","1500.00","1500.00","1500.00"]
["Envolvente","Cor","","","","integrado","integrado","integrado"]
["","Material","","","","Sem estrutura","Sem estrutura","Sem estrutura"]
["Dimensões","Unidade","","Altura","mm","576","576","576"]
["","","","Largura","mm","725","925","1125"]
["","","","Profundidade","mm","126","126","126"]
["","Unidade embalada","","Altura","mm","690","690","690"]
["","","","Largura","mm","830","1030","1230"]
["","","","Profundidade","mm","210","210","210"]
["Peso","Unidade","","","kg","12","15","18"]
["","Unidade embalada","","","kg","13","16","19"]
["Acondicionamento","Material","","","","Cartão","Cartão","Cartão"]
["","Peso","","","kg","1","1","1"]
["Permutador de calor","Quantidade","","","","1","1","1"]
["","Volume da serpentina interna","","","l","0.8","1.13","1.46"]
["","Carregamento","","Pressão de funcionamento","bar","10","10","10"]
["Circuito de água","Diâmetro das ligações de tubagens","","","in","3/4","3/4","3/4"]
["","Material da tubagem","","","","COBRE","COBRE","COBRE"]
["","Pressão","Aquecimento","Máx.","bar","10","10","10"]
["Circuito de água - queda de pressão da água","Aquecimento","45/40 °C","Mín.","kPa","1.50","2.70","3.00"]
["","","","Méd.","kPa","4.30","9.30","8.90"]
["","","","Máx.","kPa","9.20","19.10","21.20"]
["","Arrefecimento","7/12 °C","Mín.","kPa","1.90","2.70","2.50"]
["","","","Méd.","kPa","4.30","9.90","8.80"]
["","","","Máx.","kPa","8.20","17.10","18.00"]
["Circuito de água - caudal de água","Aquecimento","45/40 °C","Mín.","kg/h","140.00","210.00","260.00"]
["","","","Méd.","kg/h","270.00","380.00","450.00"]
["","","","Máx.","kg/h","390.00","530.00","660.00"]
["","Arrefecimento","7/12 °C","Mín.","kg/h","130.00","200.00","230.00"]
["","","","Méd.","kg/h","230.00","360.00","410.00"]
["","","","Máx.","kg/h","360.00","480.00","570.00"]
["Nível de potência sonora","Mín.","","","dBA","35","36","36"]
["","Méd.","","","dBA","45","46","47"]
["","Máx.","","","dBA","53.0","54.0","55.0"]
["Limite de funcionamento","Aquecimento","Lado da água","Mín.","°C","30","30","30"]
["","","","Máx.","°C","85","85","85"]
["","Arrefecimento","Lado da água","Mín.","°C","5","5","5"]
["","","","Máx.","°C","18","18","18"]
["","Instalação no interior","Ambiente","Mín.","° CBs","0","0","0"]
["","","","Máx.","° CBs","45","45","45"]
["Sistemas de controlo","Controlo remoto por infravermelhos","","","","Não","Não","Não"]
["","Incorporado na unidade interior","","","","Sim","Sim","Sim"]
["Alimentação elétrica","Fase","","","","1~","1~","1~"]
["Alimentação eléctrica","Frequência","","","Hz","50","50","50"]
["","Tensão","","","V","230","230","230"]
["Consumo de energia eléctrica","Máx.","","","W","19","20","29"]
["","Standby","","","W","3","4","5"]
["Corrente","Corrente de funcionamento máxima","","Aquecimento","A","0.16","0.18","0.26"]
["","Corrente máxima de funcionamento","","Arrefecimento","A","0.16","0.18","0.26"]