{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":11,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXV-ATV3R"]
[]
[]
[]
[]
["","","","","","FWXV10ABTV3R","FWXV10AATV3R","FWXV15ABTV3R","FWXV15AATV3R","FWXV20ABTV3R","FWXV20AATV3R"]
["Capacidade de arrefecimento","7/12 °C","","Mín.","kW","0.78","0.66","1.10","1.30","1.13","1.82"]
["","","","Méd.","kW","1.11","1.36","1.65","2.16","1.98","2.52"]
["","","","Máx.","kW","1.62","1.77","2.64","2.89","2.99","3.20"]
["Capacidade de arrefecimento sensível","7/12 °C","","Mín.","kW","0.58","0.39","0.82","0.99","0.85","1.22"]
["","","","Méd.","kW","0.71","0.98","1.15","1.53","1.55","1.55"]
["","","","Máx.","kW","1.25","1.33","1.91","2.10","2.33","1.78"]
["Capacidade de aquecimento","45/40 °C","","Mín.","kW","0.87","0.95","1.12","1.24","1.11","1.90"]
["","","","Capacidade de aquecimento-=-45/40 °C-=-Méd.-=-kW","kW","1.27","1.63","1.83","2.33","2.32","3.05"]
["","","","Máx.","kW","1.96","2.18","2.86","3.11","3.50","3.88"]
["Potência absorvida","Mín.","","","kW","0.01","0","0.01","0","0.01","0.01"]
["","Méd.","","","kW","0.01","","0.01","","0.01"]
["","Máx.","","","kW","0.02","0.02","0.03","0.02","0.03","0.03"]
["Velocidade do ventilador","Mín.","","","rpm","720.00","118.00","720.00","180.00","720.00","246.00"]
["","Méd.","","","rpm","1220.00","210.00","1220.00","318.00","1220.00","410.00"]
["","Velocidade do ventilador-=-Máx.-=-rpm","","","rpm","1700.00","294.00","1700.00","438.00","1700.00","566.00"]
["Envolvente","Cor","","","","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003"]
["","Material","","","","Folha de metal","Folha de metal","Folha de metal","Folha de metal","Folha de metal","Folha de metal"]
["Dimensões","Unidade","","Altura","mm","601","601","601","601","601","601"]
["","","","Largura","mm","999","999","1199","1200","1399","1400"]
["","","","Profundidade","mm","135","135","135","135","135","135"]
["","Unidade embalada","","Altura","mm","690","690","690","690","690","690"]
["","","","Largura","mm","1230","1230","1430","1430","1630","1630"]
["","","","Profundidade","mm","210","210","210","210","210","210"]
["Peso","Unidade","","","kg","20","20","23","23","26","26"]
["","Unidade embalada","","","kg","21","21","24","24","27","27"]
["Acondicionamento","Material","","","","Cartão","Cartão","Cartão","Cartão","Cartão","Cartão"]
["","Peso","","","kg","1","1","1","1","1","1"]
["Permutador de calor","Quantidade","","","","1","1","1","1","1","1"]
["","Volume da serpentina interna","","","l","0.8","0.8","1.1","1.1","1.5","1.5"]
["","Carregamento","","Pressão de funcionamento","bar","10","10","10","10","10","10"]
["Circuito de água","Diâmetro das ligações de tubagens","","","in","3/4","3/4","3/4","3/4","3/4","3/4"]
["","Material da tubagem","","","","COBRE","Bronze(CW617N)","COBRE","Bronze(CW617N)","COBRE","Bronze(CW617N)"]
["","Pressão","Aquecimento","Máx.","bar","10","10","10","10","10","10"]
["Circuito de água - queda de pressão da água","Aquecimento","45/40 °C","Mín.","kPa","7.00","1.30","9.00","8.60","8.00","3.80"]
["","","","Méd.","kPa","8.00","4.20","14.00","3.30","15.00","11.20"]
["","","","Máx.","kPa","11.00","7.20","23.00","11.50","22.00","21.30"]
["","Arrefecimento","7/12 °C","Mín.","kPa","7.00","1.20","9.00","4.30","8.00","2.10"]
["","","","Méd.","kPa","8.00","2.80","14.00","19.30","15.00","13.10"]
["","","","Máx.","kPa","11.00","2.90","23.00","27.00","22.00","24.00"]
["Circuito de água - caudal de água","Aquecimento","45/40 °C","Mín.","kg/h","150.00","163.50","200.00","212.50","190.00","327.00"]
["","","","Méd.","kg/h","220.00","280.30","320.00","401.10","400.00","524.60"]
["","","","Máx.","kg/h","340.00","374.10","500.00","534.50","610.00","667.50"]
["","Arrefecimento","7/12 °C","Mín.","kg/h","130.00","113.50","190.00","223.70","190.00","313.00"]
["","","","Méd.","kg/h","190.00","234.10","280.00","371.70","340.00","433.60"]
["","","","Máx.","kg/h","280.00","303.60","450.00","496.60","510.00","550.60"]
["Nível de potência sonora","Mín.","","","dBA","40","34","42","35","43","35"]
["","Méd.","","","dBA","47","43","49","43","50","44"]
["","Máx.","","","dBA","56.0","51.0","57.0","53.0","58.0","55.0"]
["Limite de funcionamento","Aquecimento","Lado da água","Mín.","°C","30","30","30","30","30","30"]
["","","","Máx.","°C","85","85","85","85","85","85"]
["","Arrefecimento","Lado da água","Mín.","°C","5","5","5","5","5","5"]
["","","","Máx.","°C","18","18","18","18","18","18"]
["","Instalação no interior","Ambiente","Mín.","° CBs","0","0","0","0","0","0"]
["","","","Máx.","° CBs","45","45","45","45","45","45"]
["Sistemas de controlo","Controlo remoto por infravermelhos","","","","Não","Não","Não","Não","Não","Não"]
["","Incorporado na unidade interior","","","","Sim","Sim","Sim","Sim","Sim","Sim"]
["Alimentação elétrica","Fase","","","","1~","1~","1~","1~","1~","1~"]
["Alimentação eléctrica","Frequência","","","Hz","50","50","50","50","50","50"]
["","Tensão","","","V","230","230","230","230","230","230"]
["Consumo de energia eléctrica","Máx.","","","W","19","19","25","20","31","29"]
["","Standby","","","W","3","3","4","4","5","5"]
["Corrente","Corrente de funcionamento máxima","","Aquecimento","A","0.15","0.2","0.21","0.2","0.27","0.3"]
["","Corrente máxima de funcionamento","","Arrefecimento","A","0.15","0.2","0.21","0.2","0.27","0.3"]